## Sheet1
Battery specification Model | ES2500 | ES5100 | ES7600 | ES10200
VOLTAGE AND CAPACITY | 51.2V/50Ah | 51.2/100Ah | 51.2/150Ah | 51.2V/200Ah
Nominal voltage | 51.2V | 51.2V | 51.2V | 51.2V
Nominal capacity @ 25°C* | 50Ah | 100Ah | 150Ah | 200Ah
Nominal capacity @ 0°C* | 40Ah | 80Ah | 120Ah | 160Ah
Nominal capacity @ -20°C* | 25Ah | 50Ah | 75Ah | 100Ah
Nominal energy @ 25°C* | 2560Wh | 5120Wh | 7680Wh | 10240Wh
*Discharge current | ≤1C
CYCLE LIFE (capacity ≥ 80% of nominal) | 80% DOD 3000 cycles 70% DOD 5000 cycles 50% DOD 6000 cycles DISCHARGE
Maximum continuous discharge current | 50A | 100A | 150A | 200A
Recommended continuous discharge current | ≤50A | ≤100A | ≤150A | ≤200A
End of discharge voltage | 40V | 40V | 40V | 40V
OPERATING CONDITIONS
Operating temperature Discharge: | -20°C to +50°C, Charge: +5°C to +50°C
Storage temperature | -25°C to 45°C
Humidity (non-condensing) | Max. 95%
Protection class | IP 22
Charge voltage | 56V
Maximum charge current | 50A | 100A | 150A | 200A
Recommended charge current | ≤50A | ≤100A | ≤150A | ≤200A
OTHER
Max storage time @ 25°C* 3 year BMS connection Male + female cable with M8 circular connector, length 50cm
Dimensions (LxWxH) mm | 483 x 440 x 134 | 483 x 440 x 223 | 483 x 440 x 223 | 483 x 440 x 267
Weight | 30kg | 50kg | 80kg | 100kg
*When fully charged